## Instructions
New Jersey Turnpike Authority
MEMORANDUM
April 16 2009
TO: | All Design Engineers
RE: | Standard Voltage Drop Computation Form
Version 001 - Document Issuance
The Authority’s Standard Voltage Drop Computation Forms 1 and 2 follow on the attached worksheets. For additional information regarding the use of the Utility Status Schedule consult Section 7 of the Design Manual. Click the Tabs at the bottom of this sheet titled "Form 1 - Calculations" and "Form 2 - Sketch and Details" to access the document.
NOTE: This Excel document has been created to aid designers in submitting Voltage Drop Calculations in a format that is consistent with the Design Manual. Calculations and formulas have not been included, and sample information is shown for informational purposes only. It is the designer's responsibility to replace all sample information shown with project specific data that has been accurately analyzed and properly designed to meet Authority Standards.

## Form 1 - Calculations
New Jersey Turnpike Authority
Standard Voltage Drop Computation Form 1 - Calculations
XYZ Engineering Company |  |  | Made by |  | Date | CIRCUIT # | 3
100 Main Street |  |  | XXXXXXXXXX |  | 2003-01-02 | PHASE # | B
Hackensack, NJ 07601 |  |  | Checked by |  | Date | VOLTAGE # | 277 V
Contract No: | T300.019 |  | XXXXXXXXXX |  | 2003-01-03
Name: | Interchange 19 Reconstruction |  | Backchecked by |  | Date | Sheet Number
|  |  | XXXXXXXXXX |  | 2003-01-05 | 1 of 2
Instructions:
Calculations shall be performed for each circuit branch separately, including all existing lamps and loads, if any are connected to the circuit. Select worst case branch voltage drop to determine total circuit voltage drop. DO NOT TOTAL ALL DROPS. Use NEC Chapter 9, Table 9 to determine appropriate resistance values, taking into account overall circuit Power Factor as described in the footnotes to the Table. Use additional forms if required for long circuits. Complete one complete set of forms for each circuit and phase.
Section | From | To | Current | Distance | Ohms/K ft | Z=2xLx0.001xΩ | Vd=IxZ
|  |  | I | L | Ω | Z | Vd
BRANCH A
1 | Panel | JB1 | 8.77 | 500 | 0.2 | 0.2 | 1.754
2 | JB1 | 1-3-B | 3.51 | 700 | 0.2 | 0.28 | 0.983
3 | 1-3-B | 4-3-B | 2.34 | 250 | 0.2 | 0.1 | 0.234
4 | 4-3-B | 7-3-B | 1.17 | 250 | 0.2 | 0.1 | 0.117
[6 empty] | TOTAL | 3.088
BRANCH B
1 | Panel | JB1 | 8.77 | 500 | 0.2 | 0.2 | 1.754
2 | JB1 | 10-3-B | 5.26 | 400 | 0.2 | 0.16 | 0.842
3 | 10-3-B | JB2 | 4.09 | 300 | 0.2 | 0.12 | 0.491
4 | JB2 | 13-3-B | 2.34 | 300 | 0.2 | 0.12 | 0.281
5 | 13-3-B | 16-3-B | 1.17 | 200 | 0.2 | 0.08 | 0.094
[6 empty] | TOTAL | 3.461
BRANCH C
1 | Panel | JB1 | 8.77 | 500 | 0.2 | 0.2 | 1.754
2 | JB1 | 10-3-B | 5.26 | 400 | 0.2 | 0.16 | 0.842
3 | 10-3-B | JB2 | 4.09 | 300 | 0.2 | 0.12 | 0.491
4 | JB2 | 19-3-B | 1.75 | 100 | 0.2 | 0.04 | 0.07
[6 empty] | TOTAL | 3.156
Worst Case Branch: |  | B
% Vd = | 3.461 V / 277 V = |  | 1.25% | is less than 3%
Comments: (To be filled in by Engineer)
All wires selected to be #2 AWG in steel conduit (Z=0.20 Ω per 1000 ft - per NEC Chapter 9, Table 9), Power Factor assumed to be 0.96.

## Form 2 - Sketch and Details
New Jersey Turnpike Authority
Standard Voltage Drop Computation Form 2 - Sketch and Details
XYZ Engineering Company |  |  | Made by |  | Date | CIRCUIT # | 3
100 Main Street |  |  | XXXXXXXXXXXX |  | 2009-01-02 | PHASE # | B
Hackensack, NJ 07601 |  |  | Checked by |  | Date | VOLTAGE # | 277 V
Contract No: | T300.019 |  | XXXXXXXXXXXX |  | 2009-01-03
Name: | Interchange 19 Reconstruction |  | Backchecked by |  | Date | Sheet Number
|  |  | XXXXXXXXXXXX |  | 2003-01-05 | 2 of 2
Circuit Information
Load Center Location: |  | Plaza Utility Building |  | Voltage: |  | 277 V
Total Load (kW): |  | 1.9 kW |  | Phase and # Wires: |  | Three Phase, 4-Wire
Wire Size: |  | #2 AWG |  | Conduit Type: |  | RMC Steel
Lamp Quantities: |  | Watts | Quantity | Watts | Quantity
|  | 70 |  | 250 | 6
|  | 100 |  | 310
|  | 150 |  | 400 | 1
|  | 200 |  | 1000
Instructions:
Show a sketch of the circuit below. Do not include any #10 AWG fixture wire.
Comments: (To be filled in by Engineer)
All wire for this circuit is #2 AWG
PANEL
JB1
1-3-B
250W
4-3-B
250W
7-3-B
250W
10-3-B
250W
JB-2
13-3-B
250W
16-3-B
250W
19-3-B
400W
500 ft
8.77 A
700 ft
3.51 A
250 ft
2.34 A
400 ft
5.26 A
300 ft
4.09 A
300 ft
2.34 A
200 ft
1.17 A
100 ft
1.75 A
250 ft
1.17 A
BRANCH B
BRANCH A
BRANCH C